Instruction for use of Ventilated Hoods

The ventilated hood is a technical protective equipment that protects you from contact and exposure to harmful chemicals and materials. The ventilated hood should be perceived as a suction box, wherein, you can have chemical consuming equipment.

In general, the difference between a ventilated hood and a fume hood, is that the fume hood has a documented effect on holding back vapors to the inside of the hood, whereas the ventilated hood has not. This is why the ventilated hood is not intended for the handling of open chemicals.

In order for the ventilated hood to provide adequate protection, it is essential for your safety that the airflow in the hood is not disturbed. Your safety therefore depends on proper working in the hood. You have a great influence on the degree of protection, and by using the following simple advice, you can ensure, that the airflow is not disturbed, and that the level of safety is high:

- Close doors and windows to the room

- Work with as low a hatch opening as possible

- Work with very gentle movements and wear a closed mantle and safety glasses

- Only keep items in the ventilated hood necessary for the work process

- Raise your equipment etc. 3-5 cm

- It should be avoided that tubes from pumps, gas lines, etc. are placed into the ventilated hood via the front door. These should be inserted via tight holes in the side / behind

- The work area is about 15 cm inside the ventilated hood, and 10 cm from the side and back edge

- Pass behind colleagues who work in the hood with very gentle movements - or wait for them to finish

- Clean the ventilated hood, when the work is done

Can be used for:

- Equipment and processes, where associated hazardous chemicals, in a closed system, can emit a small amount of diffuse harmful fumes or contaminants (i.e. by leakage) etc.

Can not be used for:

- Open handling / pouring of hazardous-labeled chemicals - a Fume Hood must be used

- Chemicals labeled with GHS06 (toxic) or GHS08 (the lung-sick man) - a Fume Hood must be used

- Live biologically active material

Specifications:

- Functions as a ventilated unit with ventilation and return to the outdoors

- At installation, the air velocity in the hatch opening is checked and set to 0.3 m/s ± 10%

- There is a control device that constantly monitors whether the air velocity in the hatch opening is correct. It gives visual and acoustic alarm if the air velocity is too high or too low. The control device looks like a small light curve - see the supplier's user manual in the info box

- The ventilation is adjusted so that there is a partial vacuum in the laboratory. The low pressure prevents contaminated air from the laboratories entering into the corridors.  Therefore, always close all doors and windows in the room

In case of alarm from the control device or power failure - Stop your experiments and remove chemicals according to your risk assessment (if it is safe). Close the hatch completely, mark the ventilated hood with the sign "Out of order", and evacuate the room / building according to local emergency instructions. The error is reported to Campus Service via the electronic error reporting system.